| MIFAB, Inc. | July 2008 |
| --- | --- |
| 1321 West 119th Street |  |
| Chicago, IL 60643-5109 |  |
| Toll Free (800) 465-2736 |  |
| Phone (773) 341-3030 | E-Mail mail@mifab.com |
| Fax (773) 341-3049 | Web Site www.mifab.com |

Product Guide Specification

Specifier Notes: This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format. The section must be carefully reviewed and edited by the Architect to meet the requirements of the project and local building code. Coordinate this section with other specification sections and the drawings. Delete all “Specifier Notes” when editing this section.

SECTION 22150

TRAP SEAL PRIMERS

Specifier Notes: This section covers MIFAB “M-500” pressure drop activated trap seal primer. Consult MIFAB for assistance in editing this section for the specific application.

PART 1	GENERAL

1.1	SECTION INCLUDES

A.	Pressure drop activated trap seal primers.

1.2	RELATED SECTIONS

Specifier Notes: Edit the following list of related sections as required for the project. List other sections with work directly related to this section.

A.	Section 22100 - Building Services Piping.

B.	Section 22400 - Plumbing Fixtures and Equipment.

1.3	REFERENCES

A.	ASSE 1018 - Trap Seal Primer Valves - Water Supply Fed.

1.4	SUBMITTALS

A.	Comply with Section 01330 - Submittal Procedures.

B.	Product Data:  Submit manufacturer's product data, including installation instructions.

1.5	DELIVERY, STORAGE, AND HANDLING

A.	Delivery:  Deliver materials to site in manufacturer's original, unopened containers and packaging, with labels clearly identifying product name and manufacturer.

B.	Storage:  Store materials in clean, dry area indoors in accordance with manufacturer's instructions.

C.	Handling:  Protect materials from damage during handling and installation.

PART 2	PRODUCTS

2.1	MANUFACTURER

Specifier Notes: Specify MIFAB, Inc. in the US or MIFAB Canada in Canada

A.	[MIFAB, Inc., 1321 West 119th Street, Chicago, IL. 60643-5109  Toll Free (800) 465-2736.]

Web Site www.mifab.com  E-Mail mail@mifab.com.

2.2	MATERIALS

Specifier Notes: Specify MR-500, M1-500, or M2-500 trap seal primers.

A.	Trap Seal Primers:  [MR-500]  [M1-500]  [M2-500] pressure drop activated, brass, trap seal primer.

1.	Tested and Certified:  ASSE 1018.

2.	Listed:  IAPMO and CSA.

3.	Operating Range:  20 to 125 psi.

4.	Line Pressure Drop to Activate:  3 psi.

5.	Inlet Opening:  1/2-inch (13-mm) male NPT.

6.	Outlet Opening:  1/2-inch (13-mm) female NPT.

7.	View Holes:  4.

8.	Filter Screen:  Removable, fine mesh brass.

9.	Seals:  O-rings.

Specifier Notes: Specify maximum number of floor drain traps served. MR-500 serves a maximum of 6. M1-500 serves a maximum of 10. M2-500 serves a maximum of 3.

10.	Floor Drain Traps Served:  Maximum of [6]  [10]  [3].

11.	Requires no adjustments and no air pre-charge.

12.	Can be disassembled in field.

PART 3	EXECUTION

3.1	EXAMINATION

A.	Examine areas to receive trap seal primers.  Notify Architect of conditions that would adversely affect installation or subsequent use.  Do not proceed with installation until unsatisfactory conditions are corrected.

3.2	PREPARATION

A.	Flush water lines before installing trap seal primers.

3.3	INSTALLATION

A.	Install trap seal primers in accordance with manufacturer's instructions.

B.	Cycle trap seal primers a minimum of 6 times to ensure optimum performance.

C.	Ensure flux and other debris is removed.

D.	Use only Teflon tape around threads.  Do not use pipe dope or paste.

E.	Do not solder fittings directly onto inlet or outlet of primer.

F.	Do not install trap seal primers closer than 40 feet apart when using same potable water supply line.

G.	Mount trap seal primers in a vertical position 1 foot above finished floor for every 20 feet of floor drain trap make-up water line.

H.	Install union connection above trap seal primers.

I.	Install line shut-off valve upstream of trap seal primers to shut off water supply when performing maintenance on trap seal primers.

J.	Avoid direct installation to prevent foreign material from entering directly into trap seal primers.

3.4	INSPECTION

A.	Use any of the 4 view holes to view water discharge from orifice, after installing and pre-cycling trap seal primers.

END OF SECTION