SIZING GUIDE FOR MIFAB LINT INTERCEPTORS

COMMERCIAL WASHERS

Single Load (similar to residential)

* 34 U.S. gallons per cycle
* discharge rate 12.4 U.S. gallons per minute (GPM)

Mid Size (18 pounder)

* 34.4 U.S. gallons per cycle
* Discharge rate 26 U.S. GPM

Triple Load

* 62.2 U.S. gallons per cycle
* Discharge rate 37 U.S. GPM

Sizing example if a laundry system had 10 single load, 2 mid size and a triple load washer:

10 machines x 12.4 GPM = 124 GPM

2 machines x 26 GPM = 52 GPM

1 machine x 37 GPM = 37 GPM

Total – 213 GPM required.

Therefore a MI-LINT-6 is required.